## Sheet1
MB Adresse | Variabel Typ | Beschreibung
40000 | uint32 | C_SunSpec_ID
40002 | uint16 | C_SunSpec_DID
40003 | uint16 | C_SunSpec_Length
40004 | String(32) | C_Manufacturer
40020 | String(32) | C_Model
40044 | String(16) | C_Version
40052 | String(32) | C_SerialNumber
40068 | uint16 | C_DeviceAddress
40069 | uint16 | C_SunSpec_DID
40070 | uint16 | C_SunSpec_Length
40071 | uint16 | I_AC_Current
40072 | uint16 | I_AC_CurrentA
40073 | uint16 | I_AC_CurrentB
40074 | uint16 | I_AC_CurrentC
40075 | int16 | I_AC_Current_SF
40076 | uint16 | I_AC_VoltageAB
40077 | uint16 | I_AC_VoltageBC
40078 | uint16 | I_AC_VoltageCA
40079 | uint16 | I_AC_VoltageAN1
40080 | uint16 | I_AC_VoltageBN1
40081 | uint16 | I_AC_VoltageCN1
40082 | int16 | I_AC_Voltage_SF
40083 | int16 | I_AC_Power
40084 | int16 | I_AC_Power_SF
40085 | uint16 | I_AC_Frequency
40086 | int16 | I_AC_Frequency_SF
40087 | int16 | I_AC_VA
40088 | int16 | I_AC_VA_SF
40089 | int16 | I_AC_VAR
40090 | int16 | I_AC_VAR_SF
40091 | int16 | I_AC_PF
40092 | int16 | I_AC_PF_SF
40093 | acc32 | I_AC_Energy_WH
40095 | uint16 | I_AC_Energy_WH_SF
40096 | uint16 | I_DC_Current
40097 | int16 | I_DC_Current_SF
40098 | uint16 | I_DC_Voltage
40099 | int16 | I_DC_Voltage_SF
40100 | int16 | I_DC_Power
40101 | int16 | I_DC_Power_SF
40103 | int16 | I_Temp_Sink
40106 | int16 | I_Temp_SF
40107 | uint16 | I_Status
40108 | uint16 | I_Status_Vendor
40121 | uint16 | C_SunSpec_DID
40122 | uint16 | C_SunSpec_Length
40123 | String(32) | C_Manufacturer
40139 | String(32) | C_Model
40155 | String(16) | C_Option
40163 | String(16) | C_Version
40171 | String(32) | C_SerialNumber
40187 | uint16 | C_DeviceAddress
40188 | uint16 | C_SunSpec_DID
40189 | uint16 | C_SunSpec_Length
40190 | int16 | M_AC_Current
40191 | int16 | M_AC_Current_A
40192 | int16 | M_AC_Current_B
40193 | int16 | M_AC_Current_C
40194 | int16 | M_AC_Current_SF
40195 | int16 | M_AC_Voltage_LN
40196 | int16 | M_AC_Voltage_AN
40197 | int16 | M_AC_Voltage_BN
40198 | int16 | M_AC_Voltage_CN
40199 | int16 | M_AC_Voltage_LL
40200 | int16 | M_AC_Voltage_AB
40201 | int16 | M_AC_Voltage_BC
40202 | int16 | M_AC_Voltage_CA
40203 | int16 | M_AC_Voltage_SF
40204 | int16 | M_AC_Freq
40205 | int16 | M_AC_Freq_SF
40206 | int16 | M_AC_Power
40207 | int16 | M_AC_Power_A
40208 | int16 | M_AC_Power_B
40209 | int16 | M_AC_Power_C
40210 | int16 | M_AC_Power_SF
40211 | int16 | M_AC_VA
40212 | int16 | M_AC_VA_A
40213 | int16 | M_AC_VA_B
40214 | int16 | M_AC_VA_C
40215 | int16 | M_AC_VA_SF
40216 | int16 | M_AC_VAR
40217 | int16 | M_AC_VAR_A
40218 | int16 | M_AC_VAR_B
40219 | int16 | M_AC_VAR_C
40220 | int16 | M_AC_VAR_SF
40221 | int16 | M_AC_PF
40222 | int16 | M_AC_PF_A
40223 | int16 | M_AC_PF_B
40224 | int16 | M_AC_PF_C
40225 | int16 | M_AC_PF_SF
40226 | uint32 | M_Exported
40228 | uint32 | M_Exported_A
40230 | uint32 | M_Exported_B
40232 | uint32 | M_Exported_C
40234 | uint32 | M_Imported
40236 | uint32 | M_Imported_A
40238 | uint32 | M_Imported_B
40240 | uint32 | M_Imported_C
40242 | int16 | M_Energy_W_SF
40243 | uint32 | M_Exported_VA
40245 | uint32 | M_Exported_VA_A
40247 | uint32 | M_Exported_VA_B
40249 | uint32 | M_Exported_VA_C
40251 | uint32 | M_Imported_VA
40253 | uint32 | M_Imported_VA_A
40255 | uint32 | M_Imported_VA_B
40257 | uint32 | M_Imported_VA_C
40259 | int16 | M_Energy_VA_SF
40260 | uint32 | M_Import_VARh_Q1
40262 | uint32 | M_Import_VARh_Q1A
40264 | uint32 | M_Import_VARh_Q1B
40266 | uint32 | M_Import_VARh_Q1C
40268 | uint32 | M_Import_VARh_Q2
40270 | uint32 | M_Import_VARh_Q2A
40272 | uint32 | M_Import_VARh_Q2B
40274 | uint32 | M_Import_VARh_Q2C
40276 | uint32 | M_Export_VARh_Q3
40278 | uint32 | M_Export_VARh_Q3A
40280 | uint32 | M_Export_VARh_Q3B
40282 | uint32 | M_Export_VARh_Q3C
40284 | uint32 | M_Export_VARh_Q4
40286 | uint32 | M_Export_VARh_Q4A
40288 | uint32 | M_Export_VARh_Q4B
40290 | uint32 | M_Export_VARh_Q4C
40292 | int16 | M_Energy_VAR_SF
40293 | uint32 | M_Events
40295 | uint16 | C_SunSpec_DID
40296 | uint16 | C_SunSpec_Length
40297 | String(32) | C_Manufacturer
40313 | String(32) | C_Model
40329 | String(16) | C_Option
40337 | String(16) | C_Version
40345 | String(32) | C_SerialNumber
40361 | uint16 | C_DeviceAddress
40362 | uint16 | C_SunSpec_DID
40363 | uint16 | C_SunSpec_Length
40364 | int16 | M_AC_Current
40365 | int16 | M_AC_Current_A
40366 | int16 | M_AC_Current_B
40367 | int16 | M_AC_Current_C
40368 | int16 | M_AC_Current_SF
40369 | int16 | M_AC_Voltage_LN
40370 | int16 | M_AC_Voltage_AN
40371 | int16 | M_AC_Voltage_BN
40372 | int16 | M_AC_Voltage_CN
40373 | int16 | M_AC_Voltage_LL
40374 | int16 | M_AC_Voltage_AB
40375 | int16 | M_AC_Voltage_BC
40376 | int16 | M_AC_Voltage_CA
40377 | int16 | M_AC_Voltage_SF
40378 | int16 | M_AC_Freq
40379 | int16 | M_AC_Freq_SF
40380 | int16 | M_AC_Power
40381 | int16 | M_AC_Power_A
40382 | int16 | M_AC_Power_B
40383 | int16 | M_AC_Power_C
40384 | int16 | M_AC_Power_SF
40385 | int16 | M_AC_VA
40386 | int16 | M_AC_VA_A
40387 | int16 | M_AC_VA_B
40388 | int16 | M_AC_VA_C
40389 | int16 | M_AC_VA_SF
40390 | int16 | M_AC_VAR
40391 | int16 | M_AC_VAR_A
40392 | int16 | M_AC_VAR_B
40393 | int16 | M_AC_VAR_C
40394 | int16 | M_AC_VAR_SF
40395 | int16 | M_AC_PF
40396 | int16 | M_AC_PF_A
40397 | int16 | M_AC_PF_B
40398 | int16 | M_AC_PF_C
40399 | int16 | M_AC_PF_SF
40400 | uint32 | M_Exported
40402 | uint32 | M_Exported_A
40404 | uint32 | M_Exported_B
40406 | uint32 | M_Exported_C
40408 | uint32 | M_Imported
40410 | uint32 | M_Imported_A
40412 | uint32 | M_Imported_B
40414 | uint32 | M_Imported_C
40416 | int16 | M_Energy_W_SF
40417 | uint32 | M_Exported_VA
40419 | uint32 | M_Exported_VA_A
40421 | uint32 | M_Exported_VA_B
40423 | uint32 | M_Exported_VA_C
40425 | uint32 | M_Imported_VA
40427 | uint32 | M_Imported_VA_A
40429 | uint32 | M_Imported_VA_B
40431 | uint32 | M_Imported_VA_C
40433 | int16 | M_Energy_VA_SF
40466 | int16 | M_Energy_VAR_SF
40467 | uint32 | M_Events
40469 | uint16 | C_SunSpec_DID
40470 | uint16 | C_SunSpec_Length
40472 | String(32) | C_Manufacturer
40488 | String(32) | C_Model
40504 | String(16) | C_Option
40512 | String(16) | C_Version
40520 | String(32) | C_SerialNumber
40536 | uint16 | C_DeviceAddress
40537 | uint16 | C_SunSpec_DID
40538 | uint16 | C_SunSpec_Length
40539 | int16 | M_AC_Current
40540 | int16 | M_AC_Current_A
40541 | int16 | M_AC_Current_B
40542 | int16 | M_AC_Current_C
40543 | int16 | M_AC_Current_SF
40544 | int16 | M_AC_Voltage_LN
40545 | int16 | M_AC_Voltage_AN
40546 | int16 | M_AC_Voltage_BN
40547 | int16 | M_AC_Voltage_CN
40548 | int16 | M_AC_Voltage_LL
40549 | int16 | M_AC_Voltage_AB
40550 | int16 | M_AC_Voltage_BC
40551 | int16 | M_AC_Voltage_CA
40552 | int16 | M_AC_Voltage_SF
40553 | int16 | M_AC_Freq
40554 | int16 | M_AC_Freq_SF
40555 | int16 | M_AC_Power
40556 | int16 | M_AC_Power_A
40557 | int16 | M_AC_Power_B
40558 | int16 | M_AC_Power_C
40559 | int16 | M_AC_Power_SF
40560 | int16 | M_AC_VA
40561 | int16 | M_AC_VA_A
40562 | int16 | M_AC_VA_B
40563 | int16 | M_AC_VA_C
40564 | int16 | M_AC_VA_SF
40565 | int16 | M_AC_VAR
40566 | int16 | M_AC_VAR_A
40567 | int16 | M_AC_VAR_B
40568 | int16 | M_AC_VAR_C
40569 | int16 | M_AC_VAR_SF
40570 | int16 | M_AC_PF
40571 | int16 | M_AC_PF_A
40572 | int16 | M_AC_PF_B
40573 | int16 | M_AC_PF_C
40574 | int16 | M_AC_PF_SF
40575 | uint32 | M_Exported
40577 | uint32 | M_Exported_A
40579 | uint32 | M_Exported_B
40581 | uint32 | M_Exported_C
40583 | uint32 | M_Imported
40585 | uint32 | M_Imported_A
40587 | uint32 | M_Imported_B
40589 | uint32 | M_Imported_C
40591 | int16 | M_Energy_W_SF
40592 | uint32 | M_Exported_VA
40594 | uint32 | M_Exported_VA_A
40596 | uint32 | M_Exported_VA_B
40598 | uint32 | M_Exported_VA_C
40600 | uint32 | M_Imported_VA
40602 | uint32 | M_Imported_VA_A
40604 | uint32 | M_Imported_VA_B
40606 | uint32 | M_Imported_VA_C
40608 | int16 | M_Energy_VA_SF
40610 | uint32 | M_Import_VARh_Q1
40612 | uint32 | M_Import_VARh_Q1A
40614 | uint32 | M_Import_VARh_Q1B
40616 | uint32 | M_Import_VARh_Q1C
40618 | uint32 | M_Import_VARh_Q2
40620 | uint32 | M_Import_VARh_Q2A
40622 | uint32 | M_Import_VARh_Q2B
40624 | uint32 | M_Import_VARh_Q2C
40626 | uint32 | M_Export_VARh_Q3
40628 | uint32 | M_Export_VARh_Q3A
40630 | uint32 | M_Export_VARh_Q3B
40632 | uint32 | M_Export_VARh_Q3C
40634 | uint32 | M_Export_VARh_Q4
40636 | uint32 | M_Export_VARh_Q4A
40638 | uint32 | M_Export_VARh_Q4B
40640 | uint32 | M_Export_VARh_Q4C
40642 | int16 | M_Energy_VAR_SF
40643 | uint32 | M_Events