{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":275,"n_cols":3,"rows_kept":275}
["MB Adresse","Variabel Typ","Beschreibung"]
[40000,"uint32","C_SunSpec_ID"]
[40002,"uint16","C_SunSpec_DID"]
[40003,"uint16","C_SunSpec_Length"]
[40004,"String(32)","C_Manufacturer"]
[40020,"String(32)","C_Model"]
[40044,"String(16)","C_Version"]
[40052,"String(32)","C_SerialNumber"]
[40068,"uint16","C_DeviceAddress"]
[40069,"uint16","C_SunSpec_DID"]
[40070,"uint16","C_SunSpec_Length"]
[40071,"uint16","I_AC_Current"]
[40072,"uint16","I_AC_CurrentA"]
[40073,"uint16","I_AC_CurrentB"]
[40074,"uint16","I_AC_CurrentC"]
[40075,"int16","I_AC_Current_SF"]
[40076,"uint16","I_AC_VoltageAB"]
[40077,"uint16","I_AC_VoltageBC"]
[40078,"uint16","I_AC_VoltageCA"]
[40079,"uint16","I_AC_VoltageAN1"]
[40080,"uint16","I_AC_VoltageBN1"]
[40081,"uint16","I_AC_VoltageCN1"]
[40082,"int16","I_AC_Voltage_SF"]
[40083,"int16","I_AC_Power"]
[40084,"int16","I_AC_Power_SF"]
[40085,"uint16","I_AC_Frequency"]
[40086,"int16","I_AC_Frequency_SF"]
[40087,"int16","I_AC_VA"]
[40088,"int16","I_AC_VA_SF"]
[40089,"int16","I_AC_VAR"]
[40090,"int16","I_AC_VAR_SF"]
[40091,"int16","I_AC_PF"]
[40092,"int16","I_AC_PF_SF"]
[40093,"acc32","I_AC_Energy_WH"]
[40095,"uint16","I_AC_Energy_WH_SF"]
[40096,"uint16","I_DC_Current"]
[40097,"int16","I_DC_Current_SF"]
[40098,"uint16","I_DC_Voltage"]
[40099,"int16","I_DC_Voltage_SF"]
[40100,"int16","I_DC_Power"]
[40101,"int16","I_DC_Power_SF"]
[40103,"int16","I_Temp_Sink"]
[40106,"int16","I_Temp_SF"]
[40107,"uint16","I_Status"]
[40108,"uint16","I_Status_Vendor"]
[40121,"uint16","C_SunSpec_DID"]
[40122,"uint16","C_SunSpec_Length"]
[40123,"String(32)","C_Manufacturer"]
[40139,"String(32)","C_Model"]
[40155,"String(16)","C_Option"]
[40163,"String(16)","C_Version"]
[40171,"String(32)","C_SerialNumber"]
[40187,"uint16","C_DeviceAddress"]
[40188,"uint16","C_SunSpec_DID"]
[40189,"uint16","C_SunSpec_Length"]
[40190,"int16","M_AC_Current"]
[40191,"int16","M_AC_Current_A"]
[40192,"int16","M_AC_Current_B"]
[40193,"int16","M_AC_Current_C"]
[40194,"int16","M_AC_Current_SF"]
[40195,"int16","M_AC_Voltage_LN"]
[40196,"int16","M_AC_Voltage_AN"]
[40197,"int16","M_AC_Voltage_BN"]
[40198,"int16","M_AC_Voltage_CN"]
[40199,"int16","M_AC_Voltage_LL"]
[40200,"int16","M_AC_Voltage_AB"]
[40201,"int16","M_AC_Voltage_BC"]
[40202,"int16","M_AC_Voltage_CA"]
[40203,"int16","M_AC_Voltage_SF"]
[40204,"int16","M_AC_Freq"]
[40205,"int16","M_AC_Freq_SF"]
[40206,"int16","M_AC_Power"]
[40207,"int16","M_AC_Power_A"]
[40208,"int16","M_AC_Power_B"]
[40209,"int16","M_AC_Power_C"]
[40210,"int16","M_AC_Power_SF"]
[40211,"int16","M_AC_VA"]
[40212,"int16","M_AC_VA_A"]
[40213,"int16","M_AC_VA_B"]
[40214,"int16","M_AC_VA_C"]
[40215,"int16","M_AC_VA_SF"]
[40216,"int16","M_AC_VAR"]
[40217,"int16","M_AC_VAR_A"]
[40218,"int16","M_AC_VAR_B"]
[40219,"int16","M_AC_VAR_C"]
[40220,"int16","M_AC_VAR_SF"]
[40221,"int16","M_AC_PF"]
[40222,"int16","M_AC_PF_A"]
[40223,"int16","M_AC_PF_B"]
[40224,"int16","M_AC_PF_C"]
[40225,"int16","M_AC_PF_SF"]
[40226,"uint32","M_Exported"]
[40228,"uint32","M_Exported_A"]
[40230,"uint32","M_Exported_B"]
[40232,"uint32","M_Exported_C"]
[40234,"uint32","M_Imported"]
[40236,"uint32","M_Imported_A"]
[40238,"uint32","M_Imported_B"]
[40240,"uint32","M_Imported_C"]
[40242,"int16","M_Energy_W_SF"]
[40243,"uint32","M_Exported_VA"]
[40245,"uint32","M_Exported_VA_A"]
[40247,"uint32","M_Exported_VA_B"]
[40249,"uint32","M_Exported_VA_C"]
[40251,"uint32","M_Imported_VA"]
[40253,"uint32","M_Imported_VA_A"]
[40255,"uint32","M_Imported_VA_B"]
[40257,"uint32","M_Imported_VA_C"]
[40259,"int16","M_Energy_VA_SF"]
[40260,"uint32","M_Import_VARh_Q1"]
[40262,"uint32","M_Import_VARh_Q1A"]
[40264,"uint32","M_Import_VARh_Q1B"]
[40266,"uint32","M_Import_VARh_Q1C"]
[40268,"uint32","M_Import_VARh_Q2"]
[40270,"uint32","M_Import_VARh_Q2A"]
[40272,"uint32","M_Import_VARh_Q2B"]
[40274,"uint32","M_Import_VARh_Q2C"]
[40276,"uint32","M_Export_VARh_Q3"]
[40278,"uint32","M_Export_VARh_Q3A"]
[40280,"uint32","M_Export_VARh_Q3B"]
[40282,"uint32","M_Export_VARh_Q3C"]
[40284,"uint32","M_Export_VARh_Q4"]
[40286,"uint32","M_Export_VARh_Q4A"]
[40288,"uint32","M_Export_VARh_Q4B"]
[40290,"uint32","M_Export_VARh_Q4C"]
[40292,"int16","M_Energy_VAR_SF"]
[40293,"uint32","M_Events"]
[40295,"uint16","C_SunSpec_DID"]
[40296,"uint16","C_SunSpec_Length"]
[40297,"String(32)","C_Manufacturer"]
[40313,"String(32)","C_Model"]
[40329,"String(16)","C_Option"]
[40337,"String(16)","C_Version"]
[40345,"String(32)","C_SerialNumber"]
[40361,"uint16","C_DeviceAddress"]
[40362,"uint16","C_SunSpec_DID"]
[40363,"uint16","C_SunSpec_Length"]
[40364,"int16","M_AC_Current"]
[40365,"int16","M_AC_Current_A"]
[40366,"int16","M_AC_Current_B"]
[40367,"int16","M_AC_Current_C"]
[40368,"int16","M_AC_Current_SF"]
[40369,"int16","M_AC_Voltage_LN"]
[40370,"int16","M_AC_Voltage_AN"]
[40371,"int16","M_AC_Voltage_BN"]
[40372,"int16","M_AC_Voltage_CN"]
[40373,"int16","M_AC_Voltage_LL"]
[40374,"int16","M_AC_Voltage_AB"]
[40375,"int16","M_AC_Voltage_BC"]
[40376,"int16","M_AC_Voltage_CA"]
[40377,"int16","M_AC_Voltage_SF"]
[40378,"int16","M_AC_Freq"]
[40379,"int16","M_AC_Freq_SF"]
[40380,"int16","M_AC_Power"]
[40381,"int16","M_AC_Power_A"]
[40382,"int16","M_AC_Power_B"]
[40383,"int16","M_AC_Power_C"]
[40384,"int16","M_AC_Power_SF"]
[40385,"int16","M_AC_VA"]
[40386,"int16","M_AC_VA_A"]
[40387,"int16","M_AC_VA_B"]
[40388,"int16","M_AC_VA_C"]
[40389,"int16","M_AC_VA_SF"]
[40390,"int16","M_AC_VAR"]
[40391,"int16","M_AC_VAR_A"]
[40392,"int16","M_AC_VAR_B"]
[40393,"int16","M_AC_VAR_C"]
[40394,"int16","M_AC_VAR_SF"]
[40395,"int16","M_AC_PF"]
[40396,"int16","M_AC_PF_A"]
[40397,"int16","M_AC_PF_B"]
[40398,"int16","M_AC_PF_C"]
[40399,"int16","M_AC_PF_SF"]
[40400,"uint32","M_Exported"]
[40402,"uint32","M_Exported_A"]
[40404,"uint32","M_Exported_B"]
[40406,"uint32","M_Exported_C"]
[40408,"uint32","M_Imported"]
[40410,"uint32","M_Imported_A"]
[40412,"uint32","M_Imported_B"]
[40414,"uint32","M_Imported_C"]
[40416,"int16","M_Energy_W_SF"]
[40417,"uint32","M_Exported_VA"]
[40419,"uint32","M_Exported_VA_A"]
[40421,"uint32","M_Exported_VA_B"]
[40423,"uint32","M_Exported_VA_C"]
[40425,"uint32","M_Imported_VA"]
[40427,"uint32","M_Imported_VA_A"]
[40429,"uint32","M_Imported_VA_B"]
[40431,"uint32","M_Imported_VA_C"]
[40433,"int16","M_Energy_VA_SF"]
[40466,"int16","M_Energy_VAR_SF"]
[40467,"uint32","M_Events"]
[40469,"uint16","C_SunSpec_DID"]
[40470,"uint16","C_SunSpec_Length"]
[40472,"String(32)","C_Manufacturer"]
[40488,"String(32)","C_Model"]
[40504,"String(16)","C_Option"]
[40512,"String(16)","C_Version"]
[40520,"String(32)","C_SerialNumber"]
[40536,"uint16","C_DeviceAddress"]
[40537,"uint16","C_SunSpec_DID"]
[40538,"uint16","C_SunSpec_Length"]
[40539,"int16","M_AC_Current"]
[40540,"int16","M_AC_Current_A"]
[40541,"int16","M_AC_Current_B"]
[40542,"int16","M_AC_Current_C"]
[40543,"int16","M_AC_Current_SF"]
[40544,"int16","M_AC_Voltage_LN"]
[40545,"int16","M_AC_Voltage_AN"]
[40546,"int16","M_AC_Voltage_BN"]
[40547,"int16","M_AC_Voltage_CN"]
[40548,"int16","M_AC_Voltage_LL"]
[40549,"int16","M_AC_Voltage_AB"]
[40550,"int16","M_AC_Voltage_BC"]
[40551,"int16","M_AC_Voltage_CA"]
[40552,"int16","M_AC_Voltage_SF"]
[40553,"int16","M_AC_Freq"]
[40554,"int16","M_AC_Freq_SF"]
[40555,"int16","M_AC_Power"]
[40556,"int16","M_AC_Power_A"]
[40557,"int16","M_AC_Power_B"]
[40558,"int16","M_AC_Power_C"]
[40559,"int16","M_AC_Power_SF"]
[40560,"int16","M_AC_VA"]
[40561,"int16","M_AC_VA_A"]
[40562,"int16","M_AC_VA_B"]
[40563,"int16","M_AC_VA_C"]
[40564,"int16","M_AC_VA_SF"]
[40565,"int16","M_AC_VAR"]
[40566,"int16","M_AC_VAR_A"]
[40567,"int16","M_AC_VAR_B"]
[40568,"int16","M_AC_VAR_C"]
[40569,"int16","M_AC_VAR_SF"]
[40570,"int16","M_AC_PF"]
[40571,"int16","M_AC_PF_A"]
[40572,"int16","M_AC_PF_B"]
[40573,"int16","M_AC_PF_C"]
[40574,"int16","M_AC_PF_SF"]
[40575,"uint32","M_Exported"]
[40577,"uint32","M_Exported_A"]
[40579,"uint32","M_Exported_B"]
[40581,"uint32","M_Exported_C"]
[40583,"uint32","M_Imported"]
[40585,"uint32","M_Imported_A"]
[40587,"uint32","M_Imported_B"]
[40589,"uint32","M_Imported_C"]
[40591,"int16","M_Energy_W_SF"]
[40592,"uint32","M_Exported_VA"]
[40594,"uint32","M_Exported_VA_A"]
[40596,"uint32","M_Exported_VA_B"]
[40598,"uint32","M_Exported_VA_C"]
[40600,"uint32","M_Imported_VA"]
[40602,"uint32","M_Imported_VA_A"]
[40604,"uint32","M_Imported_VA_B"]
[40606,"uint32","M_Imported_VA_C"]
[40608,"int16","M_Energy_VA_SF"]
[40610,"uint32","M_Import_VARh_Q1"]
[40612,"uint32","M_Import_VARh_Q1A"]
[40614,"uint32","M_Import_VARh_Q1B"]
[40616,"uint32","M_Import_VARh_Q1C"]
[40618,"uint32","M_Import_VARh_Q2"]
[40620,"uint32","M_Import_VARh_Q2A"]
[40622,"uint32","M_Import_VARh_Q2B"]
[40624,"uint32","M_Import_VARh_Q2C"]
[40626,"uint32","M_Export_VARh_Q3"]
[40628,"uint32","M_Export_VARh_Q3A"]
[40630,"uint32","M_Export_VARh_Q3B"]
[40632,"uint32","M_Export_VARh_Q3C"]
[40634,"uint32","M_Export_VARh_Q4"]
[40636,"uint32","M_Export_VARh_Q4A"]
[40638,"uint32","M_Export_VARh_Q4B"]
[40640,"uint32","M_Export_VARh_Q4C"]
[40642,"int16","M_Energy_VAR_SF"]
[40643,"uint32","M_Events"]