{"text_format":"3","workbook":"xlsx","n_sheets":5,"sheets":["Übersicht","02 Discrete input","01 Coil","04 Input Register","03 Holding Register"],"read":"whole","date_system":"1900"}

{"sheet":"Übersicht","index":0,"n_rows":37,"n_cols":7,"rows_kept":37}
[]
[]
["Variabeln","02 Discrete input","01 Coil","04 Input Register","03 Holding Register"]
[null,"Readonly Boolen","Writable Boolen","Readonly Integer","Writable Integer",null,"Big Endian"]
["WP","10-49","10-49","10-49","10-49"]
["CircD","50-69","50-69","50-69","50-69"]
["Circ1","70-89","70-89","70-89","70-89"]
["Circ2","90-109","90-109","90-109","90-109"]
["Circ3","110-129","110-129","110-129","110-129"]
["Circ4","130-149","130-149","130-149","130-149"]
["Circ5","230-249","230-249","230-249","230-249"]
["Circ6","250-269","250-269","250-269","250-269"]
["Boiler","150-169","150-169","150-169","150-169"]
["PSP","170-189","170-189","170-189","170-189"]
["Schwimbad","190-209","190-209","190-209","190-209"]
["Kühlen","210-229","210-229","210-229","210-229"]
["Diverses","300-350","300-350","300-350","300-350"]
["Alarm","500-700","500-700","500-700","500-700"]
["Kaskade","10000-11000","10000-11000","10000-11000","10000-11000"]
[]
[]
["1.1"]
["1.2","29.11.17"]
["1.3","19.01.18"]
["1.4","20.04.18"]
["1.5","30.08.18"]
["1.6","27.05.19"]
["1.7","02.08.19"]
["1.9","07.09.20"]
["1.10","23.10.20"]
["1.11","15.02.22"]
["1.12","26.08.22"]
["1.13"]
["1.14","24.04.23"]
["1.15","07.05.24"]
["1.16","28.06.24"]
["1.17","11.11.24"]

{"sheet":"02 Discrete input","index":1,"n_rows":56,"n_cols":13,"rows_kept":56}
["Type","MB Adresse","Variable","BMK","SWe/SWMe","Lwi)SLW","LWsp (HT)","LWasp (HT)","SWKe","LWKi","LWKsp (HT)","LWKasp","SWMpro"]
["DiscreteInput",1,"AlrmActive",null,"Störung","Störung","Störung","Störung","Störung","Störung","Störung","Störung","Störung"]
["DiscreteInput",10,"Outputs_01Cfg.Dout01",null,"Verdichter 1","Verdichter 1","Verdichter 1","Verdichter 1","Verdichter 1","Verdichter 1","Verdichter 1","Verdichter 1","Gehäuselüftung"]
["DiscreteInput",11,"Outputs_01Cfg.Dout02",null,"Verdichter 2","Verdichter 2","Verdichter 2","Verdichter 2","Verdichter 2","Verdichter 2","Verdichter 2","Verdichter 2","2WE"]
["DiscreteInput",12,"Outputs_01Cfg.Dout03",null,"4 Wege Ventil","4 Wege Ventil","4 Wege Ventil","4 Wege Ventil","4 Wege Ventil","4 Wege Ventil","4 Wege Ventil","4 Wege Ventil","TWW Elektroeinsatz"]
["DiscreteInput",13,"Outputs_01Cfg.Dout04",{"$nulls":9},"WP Betrieb"]
["DiscreteInput",14,"Outputs_01Cfg.Dout05","26M4","Pumpe Direkter Heizkreis","Pumpe Direkter Heizkreis","Pumpe Direkter Heizkreis",null,"Pumpe Direkter Heizkreis","Pumpe Direkter Heizkreis","Pumpe Direkter Heizkreis",null,"Störung"]
["DiscreteInput",15,"Outputs_01Cfg.Dout06","26Y6","Boiler Pumpe","Boiler Pumpe","Boiler Pumpe",null,"Boiler Pumpe","Boiler Pumpe","Boiler Pumpe",null,"Boiler Pumpe"]
["DiscreteInput",16,"Outputs_01Cfg.Dout07","41X2","2WE","2WE","2WE",null,"2WE","2WE","2WE",null,"Pumpe Direkter Heizkreis"]
["DiscreteInput",17,"Outputs_01Cfg.Dout08","42 E5","TWW Elektroeinsatz","TWW Elektroeinsatz","TWW Elektroeinsatz",null,"TWW Elektroeinsatz","TWW Elektroeinsatz","TWW Elektroeinsatz",null,"Schwimmbadpumpe"]
["DiscreteInput",18,"Outputs_01Cfg.Dout09","35M6","Schwimmbadpumpe","Schwimmbadpumpe","Schwimmbadpumpe","Schwimmbadpumpe","Schwimmbadpumpe","Schwimmbadpumpe","Schwimmbadpumpe","Schwimmbadpumpe"]
["DiscreteInput",19,"Outputs_01Cfg.Dout10","110X3","WP Betrieb","WP Betrieb","WP Betrieb","WP Betrieb","WP Betrieb","WP Betrieb","WP Betrieb","WP Betrieb"]
["DiscreteInput",20,"Outputs_01Cfg.Dout11","110X6","Störung","Störung","Störung","Störung","Störung","Störung","Störung","Störung","Ölsumpfheizung"]
["DiscreteInput",21,"Outputs_01Cfg.Dout12","24M2","Primärpumpe","Ventilator","Ventilator","Ventilator","Primärpumpe","Ventilator","Ventilator","Ventilator"]
["DiscreteInput",22,"Outputs_01Cfg.Dout13","25M2","Ladepumpe","Ladepumpe","Ladepumpe",null,"Ladepumpe","Ladepumpe","Ladepumpe"]
["DiscreteInput",23,"PmpGW",null,"Grundwasserpumpe",{"$nulls":3},"Grundwasserpumpe"]
["DiscreteInput",30,"Comp_0_AbleToOn",null,"Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit","Verdichter 1 bereit"]
["DiscreteInput",31,"Comp_1_AbleToOn",null,"Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit","Verdichter 2 bereit"]
["DiscreteInput",41,"cpCOe11DOut1",{"$nulls":4},"2WE",{"$nulls":3},"2WE"]
["DiscreteInput",42,"cpCOe11DOut2",{"$nulls":4},"TWW Elektroeinsatz",{"$nulls":3},"Boiler EL"]
["DiscreteInput",43,"cpCOe11DOut3",{"$nulls":4},"Boiler Pumpe",{"$nulls":3},"Boiler Pumpe"]
["DiscreteInput",44,"cpCOe11DOut4",{"$nulls":4},"Pumpe Direkter Heizkreis",{"$nulls":3},"Pumpe Direkter Heizkreis"]
["DiscreteInput",45,"cpCOe11DOut5"]
["DiscreteInput",46,"cpCOe11DOut6",{"$nulls":4},"Ladepumpe",{"$nulls":3},"Ladepumpe"]
["DiscreteInput",70,"cpCOe1DOut1","51M5","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe","HK1 Pumpe"]
["DiscreteInput",71,"cpCOe1DOut2","51Y7","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf","HK1 Mischer auf"]
["DiscreteInput",72,"cpCOe1DOut3","51Y7","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu","HK1Mischer zu"]
["DiscreteInput",90,"cpCOe1DOut4","53M5","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe","HK2 Pumpe"]
["DiscreteInput",91,"cpCOe1DOut5","53Y7","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf","HK2 Mischer auf"]
["DiscreteInput",92,"cpCOe1DOut6","53Y7","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu","HK2 Mischer zu"]
["DiscreteInput",110,"cpCOe3DOut1","61M5","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe","HK3 Pumpe"]
["DiscreteInput",111,"cpCOe3DOut2","61Y7","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf","HK3 Mischer auf"]
["DiscreteInput",112,"cpCOe3DOut3","61Y7","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu","HK3Mischer zu"]
["DiscreteInput",130,"cpCOe3DOut4","63M5","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe","HK4 Pumpe"]
["DiscreteInput",131,"cpCOe3DOut5","63Y7","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf","HK4Mischer auf"]
["DiscreteInput",132,"cpCOe3DOut6","63Y7","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu","HK4 Mischer zu"]
["DiscreteInput",230,"cpCOe4DOut1","71M5","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe","HK5 Pumpe"]
["DiscreteInput",231,"cpCOe4DOut2","71Y7","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf","HK5 Mischer auf"]
["DiscreteInput",232,"cpCOe4DOut3","71Y7","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu","HK5 Mischer zu"]
["DiscreteInput",250,"cpCOe4DOut4","73M5","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe","HK6 Pumpe"]
["DiscreteInput",251,"cpCOe4DOut5","73Y7","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf","HK6 Mischer auf"]
["DiscreteInput",252,"cpCOe4DOut6","73Y7","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu","HK6 Mischer zu"]
["DiscreteInput",150,"cpCOe5DOut1","97M4","Magroladepumpe TWW2",{"$nulls":7},"Magroladepumpe TWW2"]
["DiscreteInput",151,"cpCOe5DOut2"]
["DiscreteInput",152,"cpCOe5DOut3","95Y7","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil","TWW 1 Absperventil"]
["DiscreteInput",153,"cpCOe5DOut4","97Y7","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil","TWW 2 Absperventil"]
["DiscreteInput",154,"cpCOe5DOut5","99K3","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz","TWW 2 Elektroeinsatz"]
["DiscreteInput",155,"cpCOe5DOut6","95M5","Magroladepumpe TWW1","Magroladepumpe","Magroladepumpe","Magroladepumpe","Magroladepumpe","Magroladepumpe","Magroladepumpe","Magroladepumpe","Magroladepumpe TWW1"]
["DiscreteInput",210,"cpCOe2DOut1","82Y2","Umschaltventil Primär",{"$nulls":3},"Umschaltventil Primär",{"$nulls":3},"Umschaltventil Primär"]
["DiscreteInput",211,"cpCOe2DOut2","82Y4","Umschaltventil Sekundär",{"$nulls":3},"Umschaltventil Sekundär","Umschaltventil Sekundär","Umschaltventil Sekundär","Umschaltventil Sekundär","Umschaltventil Sekundär"]
["DiscreteInput",212,"cpCOe2DOut3",{"$nulls":5},"Ladepumpe Kühlen","Ladepumpe Kühlen","Ladepumpe Kühlen","Ladepumpe Kühlen"]
["DiscreteInput",213,"cpCOe2DOut4"]
["DiscreteInput",214,"cpCOe2DOut5"]
["DiscreteInput",215,"cpCOe2DOut6"]
["DiscreteInput",500,"Al_ND.Active","22B2","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm","Niederdruck Alarm"]
["DiscreteInput",501,"Al_HD.Active","22B4","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm","Hochdruck Alarm"]

{"sheet":"01 Coil","index":2,"n_rows":8,"n_cols":6,"rows_kept":8,"merged":[[2,4,3,4],[2,5,3,5]]}
["Type","MB Adresse","Variable",null,"Beschreibung"]
["Coil",300,"SmartGrid.SmartGrid_BMS_En",null,"SmartGrid Ansteuerung 1=BUS 0= Hardware Kontakte"]
["Coil",301,"SmartGrid.SmartGrid1_BMS",null,"0-0= Kein Offset / 0-1 Boiler und Heizung Offset                                                        1-1 Boiler Offset + E-Einsatz Sollwert Erhöht / 1-0 SG EVU Sperre               ","Offset ist pro Heizkreis und Puffer einstellbar"]
["Coil",302,"SmartGrid.SmartGrid2_BMS"]
["Coil",305,"ExtAnf.ExtReq_BMS_En_In","Heartbeat 15s"," Externe Leistungssteuerung 1=BUS 0= Hardware Kontakte"]
["Coil",306,"ExtAnf.ExtReq1_BMS_In","Heartbeat 15s","0-0=WP AUS / 0-1=Stufe 1 / 1-0 Stufe 1&2 / 1-1 Stufe 1,2 & 3","Funktion 03 310 Benutzen ab 2.2.0"]
["Coil",307,"ExtAnf.ExtReq2_BMS_In","Heartbeat 15s"]
["Coil",310,"AlarmMng.AlrmResByBms",null,"Quittierung"]

{"sheet":"04 Input Register","index":3,"n_rows":90,"n_cols":10,"rows_kept":90}
[null,"Type","MB Adresse","Variable","32 Bit","Beschreibung",null,null,"Variabel Typ"]
[null,"InputRegister",0,"MskPmpPriSetP",null,"Primärpumpe","24M2","0.0%","REAL"]
[null,"InputRegister",1,"SrcFan1SetP",null,"Ventilator",null,"0.0%","REAL"]
[null,"InputRegister",2,"MskPmpLadSetP",null,"Ladepumpe","25M2","0.0%","REAL"]
[null,"InputRegister",3,"Hydr2.PmpLadCoolOutPID",null,"Ladepumpe Kühlen",null,"0.0%","REAL"]
[null,"InputRegister",4,"Hydr2.PmpBoilerOutPID",null,"Boilerpumpe",null,"0.0%","REAL"]
[null,"InputRegister",5,"Boiler_Magro.PmpMagroOutPID",null,"Magroladepumpe 0-100%","95M5","0.0%","REAL"]
[null,"InputRegister",6,"ValveSetP_RL",null,"Kondensator Ventil","25Y7","0.0%","REAL"]
[null,"InputRegister",10,"Temp_VL_WP",null,"Gebäudeseite Wärmepumpe Vorlauf/Austritt  (Warm)","21R4","0.0°C","REAL"]
[null,"InputRegister",11,"Temp_RL_WP",null,"Gebäudeseite Wärmepumpe Rücklauf/Eintritt  (Kalt)","21R5","0.0°C","REAL"]
[null,"InputRegister",12,"Temp_VL_Sonde",null,"Umweltseite/Quelle Wärmepumpe Eintritt (Warm)","21R1","0.0°C","REAL"]
[null,"InputRegister",13,"Temp_RL_Sonde",null,"Umweltseite/Quelle Wärmepumpe Austritt (Kalt)","21R3","0.0°C","REAL"]
[null,"InputRegister",14,"TempInAir",null,"Luftmodul.1 Lufteintritttemperatur",null,"0.0°C","REAL"]
[null,"InputRegister",15,"TempEvapSurface",null,"Luftmodul.1 Lamellentemperatur",null,"0.0°C","REAL"]
[null,"InputRegister",20,"CondTemp",null,"Kondensationstemperatur",null,"0.0°C","REAL"]
[null,"InputRegister",21,"LiquidTemp",null,"Flüssigkeitstemperatur",null,"0.0°C","REAL"]
[null,"InputRegister",22,"EvapTemp",null,"Verdampfunstemperatur",null,"0.0°C","REAL"]
[null,"InputRegister",23,"SuctTemp",null,"Sauggastemperatur",null,"0.0°C","REAL"]
[null,"InputRegister",32,"EVD_EVO_2_MNG.VlvA_Info_EVD_1.EEVPosPerc/Evd_Emb.Params_EVDEMB_1.EVD.Variables.EEV_PosPercent.Val",null,"Expansionsventil A Öffnungsgrad",null,"0.0%","REAL"]
[null,"InputRegister",24,"Temp_Hgas",null,"Heisgastemperatur","21R6","0.0°C","REAL"]
[null,"InputRegister",28,"EvapTemp_EVD_VlvB",null,"Verdampfungstemperatur Verdichter 2 bei CPV",null,"0.0°C","REAL"]
[null,"InputRegister",25,"EVD_EVO_2_MNG.VlvB_Info_EVD_1.SuctTemp",null,"Sauggastemperatur 2",null,"0.0°C","REAL"]
[null,"InputRegister",33,"EVD_EVO_2_MNG.VlvB_Info_EVD_1.EEVPosPerc",null,"Expansionsventil B Öffnungsgrad",null,"0.0%","REAL"]
[null,"InputRegister",26,"Temp_VL_Gw",null,"Grundwassertemperatur VL (Warm)","23R6","0.0°C","REAL"]
[null,"InputRegister",27,"Temp_RL_Gw",null,"Grundwassertemperatur RL (Kalt)","23R7","0.0°C","REAL"]
[null,"InputRegister","29","FlwSec_m3h",null,"Durchfluss Gebäudeseite Heizen","25B6",{"v":0,"d":"0.0"},"m3/h"]
[null,"InputRegister","30","FlwSecCool_m3h",null,"Durchfluss Gebäudeseite Kühlen","81B8",{"v":0,"d":"0.0"},"m3/h"]
[null,"InputRegister",31,"FlwPri_m3h",null,"Durchfluss Umweltseite","22B7",{"v":0,"d":"0.0"},"m3/h"]
[null,"InputRegister",40,"HoursCounters.HoursNo_0","32 Bit","Betreibsstunden Verdichter 1 ",null,"0h","UDINT"]
[null,"InputRegister",42,"HoursCounters.HoursNo_1","32 Bit","Betreibsstunden Verdichter 2",null,"0h","UDINT"]
[null,"InputRegister",44,"HoursCounters.Hours_2WE","32 Bit","Betreibsstunden 2 Wäremeerzeuger",null,"0h","UDINT"]
["2024-06-26","InputRegister",46,"MskPwrReq",null,"WP Leistung in %",null,"0.0%","REAL"]
[null,"InputRegister",50,"CircD.TempCircD",null,"Rücklauftemperatur Direkterheizkreis  oder Puffertemperatur",null,"0.0°C","REAL"]
[1.17,"InputRegister",51,null,null,"Sollwert Heizen Direkterheizkreis",null,"0.0°C","REAL"]
[null,"InputRegister",70,"Temp_Circ1",null,"Vorlauftemperatur Mischerkreis 1","51R1","0.0°C","REAL"]
[1.17,"InputRegister",71,null,null,"Sollwert Heizen Mischerkreis 1",null,"0.0°C","REAL"]
[null,"InputRegister",90,"Temp_Circ2",null,"Vorlauftemperatur Mischerkreis 2","53R1","0.0°C","REAL"]
[1.17,"InputRegister",91,null,null,"Sollwert Heizen Mischerkreis 2",null,"0.0°C","REAL"]
[null,"InputRegister",110,"Temp_Circ3",null,"Vorlauftemperatur Mischerkreis 3","61R1","0.0°C","REAL"]
[1.17,"InputRegister",111,null,null,"Sollwert Heizen Mischerkreis 3",null,"0.0°C","REAL"]
[null,"InputRegister",130,"Temp_Circ4",null,"Vorlauftemperatur Mischerkreis 4","63R1","0.0°C","REAL"]
[1.17,"InputRegister",131,null,null,"Sollwert Heizen Mischerkreis 4",null,"0.0°C","REAL"]
[null,"InputRegister",230,"Temp_Circ5",null,"Vorlauftemperatur Mischerkreis 5","73R1","0.0°C","REAL"]
[1.17,"InputRegister",231,null,null,"Sollwert Heizen Mischerkreis 5",null,"0.0°C","REAL"]
[null,"InputRegister",250,"Temp_Circ6",null,"Vorlauftemperatur Mischerkreis 6","73R1","0.0°C","REAL"]
[1.17,"InputRegister",251,null,null,"Sollwert Heizen Mischerkreis 6",null,"0.0°C","REAL"]
[null,"InputRegister",150,"Temp_Boiler",null,"Trinkwarmwasserspiecher oben (Ein)","30R4","0.0°C","REAL"]
[1.17,"InputRegister",151,"HoursCounters.HoursBoiler_EL","32 Bit","Betreibsstunden 2 Wäremeerzeuger Boiler",null,"0h","UDINT"]
[null,"InputRegister",153,"Temp_Boiler_2",null,"Trinkwarmwasserspiecher unten (Aus)","95R2","0.0°C","REAL"]
[null,"InputRegister",154,"Temp_Magro_HW",null,"VL Magroladung Sekundär","95R3","0.0°C","REAL"]
[null,"InputRegister",155,"VlvMagroSetP",null,"TWW1 Magroladungventil 0-100%","95Y7","0.0%","REAL"]
[null,"InputRegister",160,"Temp_Boiler2",null,"Trinkwarmwasserspiecher 2 oben (Ein)",null,"0.0°C","REAL"]
[null,"InputRegister",161,"Temp_Boiler2_2",null,"Trinkwarmwasserspiecher 2 unten (Aus)",null,"0.0°C","REAL"]
[null,"InputRegister",162,"Temp_Magro2_HW",null,"VL Magroladung Sekundär",null,"0.0%","REAL","reserviert"]
[null,"InputRegister",163,"Boiler2_Magro.PmpMagroOutPID",{"$nulls":3},"0.0%","REAL","reserviert"]
[null,"InputRegister",164,"Boiler2_Magro.VlvMagroSetP",{"$nulls":3},"0.0%","REAL","reserviert"]
[null,"InputRegister",165,"HoursCounters.HoursBoiler2_EL","32 Bit",null,null,"0h","UDINT"]
[null,"InputRegister",170,"Temp_PSP",null,"Puffertemperatur Heizung","30R6","0.0°C","REAL"]
["2024-06-26","InputRegister",171,"WAF",null,"Maximale Anforderung Heizen an WP",null,"0.0°C","REAL"]
[null,"InputRegister",210,"Temp_PSP_Cool",null,"Puffertemperatur Kühlen","81R6","0.0°C","REAL"]
[null,"InputRegister",211,"Temp_FC_Primar_VL",null,"Umweltseite Passivkühlen Wärmetauscher Eintritt","81R3","0.0°C","REAL"]
[null,"InputRegister",212,"Temp_FC_Primar_RL",null,"Umweltseite Passivkühlen Wärmetauscher Asutritt","81R1","0.0°C","REAL"]
[null,"InputRegister",213,"Temp_FC_Sekundar_VL",null,"Gebäudeseite Passivkühlen Wärmetauscher Asutritt","81R4","0.0°C","REAL"]
[null,"InputRegister",214,"Temp_FC_Sekundar_RL",null,"Gebäudeseite Passivkühlen Wärmetauscher Eintritt","81R5","0.0°C","REAL"]
["2024-06-26","InputRegister",215,"HeatCoolReq.KAF",null,"Minimale Anforderung Kühlen an WP",null,"0.0°C","REAL"]
[null,"InputRegister",300,"Temp_ODoor",null,"Aussentemperatur","30R2","0.0°C","REAL"]
[null,"InputRegister",310,"ExtAnf.ExReqStepBMS_Out",null,"Sonderanwendungen ",null,0,"INT"]
[null,"InputRegister",311,"CompInvHz/Bldc_PowerPlus.Info_PWRP1.Info_RotorSpeed_rps","32 Bit","Hz FU Ausgang bei ABB/FUJI, rps bei Carel",null,"0.0Hz/rps","REAL"]
[null,"InputRegister",313,"CompInvA","32 Bit","Stromaufnahme FU Ausgang",null,"0.0A","REAL"]
[null,"InputRegister",315,"CompInvV","32 Bit","Spannung FU Ausgang",null,"0.0V","REAL"]
[null,"InputRegister",317,"W21_Real","32 Bit","Leistung FU Eingang kW nur FUJI FU"]
[null,"InputRegister",319,"CompInvkW","32 Bit","Leistung FU Ausgang kW",null,"0.0kW","REAL"]
[null,"InputRegister",321,"CompInv_FUJI.W181_Real","32 Bit","Energieverbrauch FU MWh nur FUJI FU"]
[null,"InputRegister","323","CompInvkWh","32 Bit","Energieverbrauch FU kWh bei ABB FU",null,"0kWh","UDINT"]
[null,"InputRegister","330","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[1]",null,"Fühlermodul Eingang 1","98R2","0.0°C","REAL"]
[null,"InputRegister","331","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[2]",null,"Fühlermodul Eingang 2","98R3","0.0°C","REAL"]
[null,"InputRegister","332","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[3]",null,"Fühlermodul Eingang 3","98R4","0.0°C","REAL"]
[null,"InputRegister","333","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[4]",null,"Fühlermodul Eingang 4","98R5","0.0°C","REAL"]
[null,"InputRegister","334","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[5]",null,"Fühlermodul Eingang 5","98R6","0.0°C","REAL"]
[null,"InputRegister","335","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[6]",null,"Fühlermodul Eingang 6","98R7","0.0°C","REAL"]
[null,"InputRegister","336","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[7]",null,"Fühlermodul Eingang 7","98R8","0.0°C","REAL"]
[null,"InputRegister","337","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[8]",null,"Fühlermodul Eingang 8","99R2","0.0°C","REAL"]
[null,"InputRegister","338","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[9]",null,"Fühlermodul Eingang 9","99R3","0.0°C","REAL"]
[null,"InputRegister","339","cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[10]",null,"Fühlermodul Eingang 10","99R4","0.0°C","REAL"]
[null,"InputRegister",510,"AlarmMng.AlrmCode1","32 Bit","Störung 1 Nummer",null,0,"UDINT"]
[null,"InputRegister",512,"AlarmMng.AlrmCode2","32 Bit","Störung 2 Nummer",null,0,"UDINT"]
[]
[]
[null,"InputRegister",500,"AUTO_MOP",null,"Sonderanwendungen "]
[null,"InputRegister",501,"CondMinCool",null,"Sonderanwendungen "]

{"sheet":"03 Holding Register","index":4,"n_rows":35,"n_cols":12,"rows_kept":35,"merged":[[0,1,0,7]]}
[null,"Achtung: Nichtflüchtiger NVM-Speicher mit begrenzter Beschreibbarkeit. Maximal\neine Variable pro Stunde beschreiben, ansonsten wird die Lebensdauer des\nControllers überdurchschnittlich verkürzt!"]
["Seit","Type","MB Adresse","Variable",null,"Beschreibung",null,"Variabel Typ"]
[null,"HoldingRegister",10,"OnOffUnitMng.UnitModus",null,"0=OFF 1=AUTO 2=Sommer 3=2WE 4=Nur Heizen",0,"INT","NVM"]
[null,"HoldingRegister",50,"CircD.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",51,"CircD.SetP_Heat_constantTemp",null,"Soll Direkter HK/WP in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",52,"CircD.BMS_SetP_Heat",null,"Soll Direkter HKD in °C","0.0°C","REAL"]
[null,"HoldingRegister",70,"Circ1.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",71,"Circ1.SetP_Heat_constantTemp",null,"Soll  HK1 in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",72,"Circ1.BMS_SetP_Heat",null,"Soll  HK1 in °C","0.0°C","REAL"]
[null,"HoldingRegister",90,"Circ2.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",91,"Circ2.SetP_Heat_constantTemp",null,"Soll  HK2 in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",92,"Circ2.BMS_SetP_Heat",null,"Soll  HK2 in °C","0.0°C","REAL"]
[null,"HoldingRegister",110,"Circ3.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",111,"Circ3.SetP_Heat_constantTemp",null,"Soll  HK3 in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",112,"Circ3.BMS_SetP_Heat",null,"Soll  HK3 in °C","0.0°C","REAL"]
[null,"HoldingRegister",130,"Circ4.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",131,"Circ4.SetP_Heat_constantTemp",null,"Soll  HK4 in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",132,"Circ4.BMS_SetP_Heat",null,"Soll  HK4 in °C","0.0°C","REAL"]
[null,"HoldingRegister",230,"Circ5.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",231,"Circ5.SetP_Heat_constantTemp",null,"Soll  HK5 in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",232,"Circ5.BMS_SetP_Heat",null,"Soll  HK5 in °C","0.0°C","REAL"]
[null,"HoldingRegister",250,"Circ6.OffsetHeat_Msk",null,"21 = 0  Min 0  Max  40",0,"UINT","NVM"]
[null,"HoldingRegister",251,"Circ6.SetP_Heat_constantTemp",null,"Soll  HK6 in °C","0.0°C","REAL","NVM"]
[1.17,"HoldingRegister",252,"Circ6.BMS_SetP_Heat",null,"Soll  HK6 in °C","0.0°C","REAL"]
[null,"HoldingRegister",150,"Boiler1.SetP_User",null,"Trinkwarmwasserspiecher 1 Sollwert","0.0°C","REAL","NVM"]
[null,"HoldingRegister",160,"Boiler2.SetP_User",null,"Trinkwarmwasserspiecher 2 Sollwert","0.0°C","REAL","NVM"]
[null,"HoldingRegister",310,"ExtAnf.ExReqStepBMS","Heartbeat 15s","0=AUS/1=Stufe1/2=Stufe2/3=Stufe3",0,"INT","Nur Sole nicht modulierend ","NoRead_WritePoll",null,"Read auf 04 310"]
["1.16","HoldingRegister",313,"ExtAnf.BMS_UnitModus",null,"0=AUS/1=Heizen/2=Kühlen",0,"INT"]
[1.17,"HoldingRegister",314,"ExtAnf.BMS_ExtSetP_PmpPri","Heartbeat 5 min","0= Aus, 1.0=1% 100.0=100%","0.0°C","REAL"]
[]
[]
[]
[]
[null,"HoldingRegister",311,"ExtAnf.ExtPwrReqBMS",null,"Leistungsanforderung an Kaskade/WP","0.0°C","REAL"]
[null,"HoldingRegister",312,"ExtAnf.ExtWP_VL_BMS",null,"Temperaturanforderung an Kaskade/WP","0.0°C","REAL"]