{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["Register_Map","Legend"],"read":"whole","date_system":"1900"}

{"sheet":"Register_Map","index":0,"n_rows":81,"n_cols":9,"rows_kept":81}
["Register_Type","Address","Length","Data_Type","Byteorder","Scaling","Offset","Tag_Name","Description"]
["IR",0,1,"INT16","AB",0.1,0,"MskPmpPriSetP","Primärpumpe"]
["IR",1,1,"INT16","AB",0.1,0,"SrcFan1SetP","Ventilator"]
["IR",2,1,"INT16","AB",0.1,0,"MskPmpLadSetP","Ladepumpe"]
["IR",3,1,"INT16","AB",0.1,0,"Hydr2.PmpLadCoolOutPID","Ladepumpe Kühlen"]
["IR",4,1,"INT16","AB",0.1,0,"Hydr2.PmpBoilerOutPID","Boilerpumpe"]
["IR",5,1,"INT16","AB",0.1,0,"Boiler_Magro.PmpMagroOutPID","Magroladepumpe 0-100%"]
["IR",6,1,"INT16","AB",0.1,0,"ValveSetP_RL","Kondensator Ventil"]
["IR",10,1,"INT16","AB",0.1,0,"Temp_VL_WP","Gebäudeseite Wärmepumpe Vorlauf/Austritt  (Warm)"]
["IR",11,1,"INT16","AB",0.1,0,"Temp_RL_WP","Gebäudeseite Wärmepumpe Rücklauf/Eintritt  (Kalt)"]
["IR",12,1,"INT16","AB",0.1,0,"Temp_VL_Sonde","Umweltseite/Quelle Wärmepumpe Eintritt (Warm)"]
["IR",13,1,"INT16","AB",0.1,0,"Temp_RL_Sonde","Umweltseite/Quelle Wärmepumpe Austritt (Kalt)"]
["IR",14,1,"INT16","AB",0.1,0,"TempInAir","Luftmodul.1 Lufteintritttemperatur"]
["IR",15,1,"INT16","AB",0.1,0,"TempEvapSurface","Luftmodul.1 Lamellentemperatur"]
["IR",20,1,"INT16","AB",0.1,0,"CondTemp","Kondensationstemperatur"]
["IR",21,1,"INT16","AB",0.1,0,"LiquidTemp","Flüssigkeitstemperatur"]
["IR",22,1,"INT16","AB",0.1,0,"EvapTemp","Verdampfunstemperatur"]
["IR",23,1,"INT16","AB",0.1,0,"SuctTemp","Sauggastemperatur"]
["IR",32,1,"INT16","AB",0.1,0,"EVD_EVO_2_MNG.VlvA_Info_EVD_1.EEVPosPerc/Evd_Emb.Params_EVDEMB_1.EVD.Variables.EEV_PosPercent.Val","Expansionsventil A Öffnungsgrad"]
["IR",24,1,"INT16","AB",0.1,0,"Temp_Hgas","Heisgastemperatur"]
["IR",28,1,"INT16","AB",0.1,0,"EvapTemp_EVD_VlvB","Verdampfungstemperatur Verdichter 2 bei CPV"]
["IR",25,1,"INT16","AB",0.1,0,"EVD_EVO_2_MNG.VlvB_Info_EVD_1.SuctTemp","Sauggastemperatur 2"]
["IR",33,1,"INT16","AB",0.1,0,"EVD_EVO_2_MNG.VlvB_Info_EVD_1.EEVPosPerc","Expansionsventil B Öffnungsgrad"]
["IR",26,1,"INT16","AB",0.1,0,"Temp_VL_Gw","Grundwassertemperatur VL (Warm)"]
["IR",27,1,"INT16","AB",0.1,0,"Temp_RL_Gw","Grundwassertemperatur RL (Kalt)"]
["IR",29,1,"INT16","AB",1,0,"FlwSec_m3h","Durchfluss Gebäudeseite Heizen"]
["IR",30,1,"INT16","AB",1,0,"FlwSecCool_m3h","Durchfluss Gebäudeseite Kühlen"]
["IR",31,1,"INT16","AB",1,0,"FlwPri_m3h","Durchfluss Umweltseite"]
["IR",40,2,"UINT32","ABCD",1,0,"HoursCounters.HoursNo_0","Betreibsstunden Verdichter 1 "]
["IR",42,2,"UINT32","ABCD",1,0,"HoursCounters.HoursNo_1","Betreibsstunden Verdichter 2"]
["IR",44,2,"UINT32","ABCD",1,0,"HoursCounters.Hours_2WE","Betreibsstunden 2 Wäremeerzeuger"]
["IR",46,1,"INT16","AB",0.1,0,"MskPwrReq","WP Leistung in %"]
["IR",50,1,"INT16","AB",0.1,0,"CircD.TempCircD","Rücklauftemperatur Direkterheizkreis  oder Puffertemperatur"]
["IR",70,1,"INT16","AB",0.1,0,"Temp_Circ1","Vorlauftemperatur Mischerkreis 1"]
["IR",90,1,"INT16","AB",0.1,0,"Temp_Circ2","Vorlauftemperatur Mischerkreis 2"]
["IR",110,1,"INT16","AB",0.1,0,"Temp_Circ3","Vorlauftemperatur Mischerkreis 3"]
["IR",130,1,"INT16","AB",0.1,0,"Temp_Circ4","Vorlauftemperatur Mischerkreis 4"]
["IR",230,1,"INT16","AB",0.1,0,"Temp_Circ5","Vorlauftemperatur Mischerkreis 5"]
["IR",250,1,"INT16","AB",0.1,0,"Temp_Circ6","Vorlauftemperatur Mischerkreis 6"]
["IR",150,1,"INT16","AB",0.1,0,"Temp_Boiler","Trinkwarmwasserspiecher oben (Ein)"]
["IR",151,2,"UINT32","ABCD",1,0,"HoursCounters.HoursBoiler_EL","Betreibsstunden 2 Wäremeerzeuger Boiler"]
["IR",153,1,"INT16","AB",0.1,0,"Temp_Boiler_2","Trinkwarmwasserspiecher unten (Aus)"]
["IR",154,1,"INT16","AB",0.1,0,"Temp_Magro_HW","VL Magroladung Sekundär"]
["IR",155,1,"INT16","AB",0.1,0,"VlvMagroSetP","TWW1 Magroladungventil 0-100%"]
["IR",160,1,"INT16","AB",0.1,0,"Temp_Boiler2","Trinkwarmwasserspiecher 2 oben (Ein)"]
["IR",161,1,"INT16","AB",0.1,0,"Temp_Boiler2_2","Trinkwarmwasserspiecher 2 unten (Aus)"]
["IR",162,1,"INT16","AB",0.1,0,"Temp_Magro2_HW","VL Magroladung Sekundär"]
["IR",163,1,"INT16","AB",0.1,0,"Boiler2_Magro.PmpMagroOutPID"]
["IR",164,1,"INT16","AB",0.1,0,"Boiler2_Magro.VlvMagroSetP"]
["IR",165,2,"UINT32","ABCD",1,0,"HoursCounters.HoursBoiler2_EL"]
["IR",170,1,"INT16","AB",0.1,0,"Temp_PSP","Puffertemperatur Heizung"]
["IR",171,1,"INT16","AB",0.1,0,"WAF","Maximale Anforderung Heizen an WP"]
["IR",210,1,"INT16","AB",0.1,0,"Temp_PSP_Cool","Puffertemperatur Kühlen"]
["IR",211,1,"INT16","AB",0.1,0,"Temp_FC_Primar_VL","Umweltseite Passivkühlen Wärmetauscher Eintritt"]
["IR",212,1,"INT16","AB",0.1,0,"Temp_FC_Primar_RL","Umweltseite Passivkühlen Wärmetauscher Asutritt"]
["IR",213,1,"INT16","AB",0.1,0,"Temp_FC_Sekundar_VL","Gebäudeseite Passivkühlen Wärmetauscher Asutritt"]
["IR",214,1,"INT16","AB",0.1,0,"Temp_FC_Sekundar_RL","Gebäudeseite Passivkühlen Wärmetauscher Eintritt"]
["IR",215,1,"INT16","AB",0.1,0,"HeatCoolReq.KAF","Minimale Anforderung Kühlen an WP"]
["IR",300,1,"INT16","AB",0.1,0,"Temp_ODoor","Aussentemperatur"]
["IR",310,1,"INT16","AB",1,0,"ExtAnf.ExReqStepBMS_Out","Sonderanwendungen "]
["IR",311,2,"FLOAT32","ABCD",1,0,"CompInvHz/Bldc_PowerPlus.Info_PWRP1.Info_RotorSpeed_rps","Hz FU Ausgang bei ABB/FUJI, rps bei Carel"]
["IR",313,2,"FLOAT32","ABCD",1,0,"CompInvA","Stromaufnahme FU Ausgang"]
["IR",315,2,"FLOAT32","ABCD",1,0,"CompInvV","Spannung FU Ausgang"]
["IR",317,2,"UINT32","ABCD",1,0,"W21_Real","Leistung FU Eingang kW nur FUJI FU"]
["IR",319,2,"FLOAT32","ABCD",1,0,"CompInvkW","Leistung FU Ausgang kW"]
["IR",321,2,"UINT32","ABCD",1,0,"CompInv_FUJI.W181_Real","Energieverbrauch FU MWh nur FUJI FU"]
["IR",323,2,"UINT32","ABCD",1,0,"CompInvkWh","Energieverbrauch FU kWh bei ABB FU"]
["IR",330,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[1]","Fühlermodul Eingang 1"]
["IR",331,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[2]","Fühlermodul Eingang 2"]
["IR",332,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[3]","Fühlermodul Eingang 3"]
["IR",333,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[4]","Fühlermodul Eingang 4"]
["IR",334,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[5]","Fühlermodul Eingang 5"]
["IR",335,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[6]","Fühlermodul Eingang 6"]
["IR",336,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[7]","Fühlermodul Eingang 7"]
["IR",337,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[8]","Fühlermodul Eingang 8"]
["IR",338,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[9]","Fühlermodul Eingang 9"]
["IR",339,1,"INT16","AB",0.1,0,"cpCOe15_Mng.ValsOut_CPCOE_1.UnivChs[10]","Fühlermodul Eingang 10"]
["IR",510,2,"UINT32","ABCD",1,0,"AlarmMng.AlrmCode1","Störung 1 Nummer"]
["IR",512,2,"UINT32","ABCD",1,0,"AlarmMng.AlrmCode2","Störung 2 Nummer"]
["IR",500,1,"UINT16","AB",1,0,"AUTO_MOP","Sonderanwendungen "]
["IR",501,1,"UINT16","AB",1,0,"CondMinCool","Sonderanwendungen "]

{"sheet":"Legend","index":1,"n_rows":21,"n_cols":3,"rows_kept":21}
["Category","Field","Allowed Values / Description"]
["Register_Type","COIL","Coils (Schreib-/Lesebits)"]
["Register_Type","DI","Discrete Inputs (nur Lesen)"]
["Register_Type","IR","Input Registers (16 Bit, Read Only)"]
["Register_Type","HR","Holding Registers (16 Bit, Read/Write)"]
["Data_Type","BOOL","1 Bit"]
["Data_Type","UINT16","Unsigned 16 Bit (1 Register)"]
["Data_Type","INT16","Signed 16 Bit (1 Register)"]
["Data_Type","UINT32","Unsigned 32 Bit (2 Register)"]
["Data_Type","INT32","Signed 32 Bit (2 Register)"]
["Data_Type","FLOAT32","IEEE 754 Float (2 Register)"]
["Data_Type","FLOAT64","IEEE 754 Double (4 Register)"]
["Byteorder","AB","16 Bit normal (kein Swap)"]
["Byteorder","ABCD","32 Bit Big-Endian"]
["Byteorder","CDAB","Word-Swap (Modbus Standard)"]
["Byteorder","BADC","Byte-Swap"]
["Byteorder","DCBA","Word + Byte Swap"]
["Scaling","-","Multiplikationsfaktor für Rohwert"]
["Offset","-","Additiver Korrekturwert"]
["Tag_Name","-","Eindeutiger Python-Variablenname"]
["Description","-","Freitext-Beschreibung"]